## Cost model analysis
Pumped hydro energy storage |  |  | Questions? Contact: | andrew.blakers@anu.edu.au
Indicative costing. This spreadsheet is not to be relied upon. Accurate costing of PHES systems requires detailed engineering, geological, hydrological, environmental, heritage and other studies. It is not known whether any particular site would be suitable or commercially feasible.
All costs are in 2024 USD, except where specified.
| Currency: USD |  | Local currency
Inflation factor (2017 to 2024) | 81%
CAPITAL COSTS (2024) |  |  | 0.67 | Exchange rate USD to local currency, default is AUD
Capital cost - power | 1020.461 | $/kW | 1523.076 | $/kW
Capital cost - energy | 16.9765 | $/kWh | 25.338 | $/kWh
Capital cost | 2720.9745 | $million | 4061.156 | $million
Cost class | AA
Cost/benchmark | 42.14% | Benchmark = Class A/B boundary
Capital costs (power & energy) expressed per kW | 2720.9745 | $/kW | 4061.156 | $/kW
Capital costs (power & energy) expressed per kWh | 27.2097 | $/kWh | 40.6116 | $/kWh
KEY INPUTS
Power rating (P) | 1000 | MW |  | Green cells are input cells
Head (height difference between reservoirs) (H) | 600 | m |  | Blue cells are default figures
Separation between reservoirs (S) | 6000 | m |  | Yellow cells are output cells
Stored energy | 100 | GWh
Water-rock volume ratio | 10 | Ratio of total impounded water to the volume of rock needed to form the twin reservoirs
Land acquisition | 0.1 | $/m2 | US$1000/Ha
Initial fill acquisition | 25 | $/ML | US$500/ML | Singapore industrial water
|  |  | US$25/ML | Bulk rural NSW water
DEFAULT INPUTS
Potential energy | E=m*g*h
Pumping efficiency (default 90%) | 88%
Generation efficiency (default 90%) | 88%
Useable fraction of the water volume (default 85%) | 85%
Cost of building a dam (default 168, 2017 value) | 168 | $/m3 | 207.4074 | $/m3 in 2024
COMPONENT CAPITAL COSTS |  |  | Fraction
Cost - reservoirs (energy storage) | 1697.6488 | $million | 62.39% | For heads >800m, two tunnels and 2 powerhouses are assumed, of half head, half power and half separation
Cost - tunnel | 451.3289 | $million | 16.59% |  | For heads >800m, two tunnels and 2 powerhouses are assumed, of half head, half power and half separation
Cost - Powerhouse | 569.1321 | $million | 20.92%
Land acquisition | 0.81851 | $million | 0.03008% |  | For Bluefield: the upper reservoir is constrained to less than half the area of the lower (existing) reservoir
Initial fill acquisition | 2.0463 | $million | 0.0752%
SYSTEM CHARACTERISTICS
Total reservoir water volume (including dead water) | 81.8509 | Gigalitres = Mm3 | 0.81851 | GL/GWh
Available reservoir water volume | 69.5733 | Gigalitres = Mm3
Rock volume required to construct the walls | 8.1851 | Gigalitres = Mm3
Slope (Head divided by separation) | 10%
Hours of operation at full power | 100 | hours
Average reservoir depth | 20 | m | 8.1851 | Ha/GWh
Combined reservoir area | 818.5092 | Ha | 10 | Ha/GL
|  |  | 3.228 | Diameter (km) for a circular reservoir
REAL DISCOUNT RATE (INFLATION-FREE)
Equity fraction | 30%
Bank debt fraction | 70%
Equity rate of return | 10%
Bank interest rate | 5%
Nominal discount rate | 6.5% | per yr | Governments can generally borrow at a lower rate
Inflation rate | 1.5%
Real discount rate (inflation-free) | 5% | per yr
ANNUAL O&M | 0.4896% | of initial capital cost per year
Annual fixed O&M per MW | 10.1358 | $million
Annual variable O&M per MWh (pump + gen) | 3.1852 | $million
SYSTEM PARAMETERS
Average purchase price of energy for storage | 20 | $/MWh
System lifetime | 100 | yrs | 200 | Cycle time (hours) and (days) | 8.3333
Pumping + generating cycles per year (average) | 43 | OK | 43.8 | Max cycles per year
Refurbishment at 20 and 40 years: net present value | 69.5803 | $million | 2.557% | of initial capital cost
RESULTS
Annual energy purchased (before pumping losses) | 4.8864 | TWh
Annual energy sold (after generation losses) | 3.784 | TWh | Local currency
Cost to purchase lost energy | 5.8264 | $/MWh | 8.6962
Capital cost | 37.1232 | $/MWh | 55.4078 | $/MWh
O&M cost | 3.5203 | $/MWh | 5.2542 | $/MWh
Levelised cost of storage | 46.47 | $/MWh | 69.3582 | $/MWh
BENCHMARK
Benchmark cost -energy | 58.0247 | $/kWh | reservoirs
Benchmark cost - power | 654.321 | $/kW | penstock, pump/turbine, generator, switchyard, transmission, control
Total cost | 6456.7901 | $million
Explore our Pumped Hydro Atlases:
https://re100.eng.anu.edu.au/
Note on B6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://www.usinflationcalculator.com/inflation/current-inflation-rates/
Note on D24: Author: https://www.pub.gov.sg/watersupply/waterprice
Note on D25: Author: https://www.ipart.nsw.gov.au/sites/default/files/cm9_documents/Final-Report-Review-of-Water-NSWs-rural-bulk-water-prices-September-2021.PDF